## **Section 8 – Operational Controls**

## Ventilation Verification and Energy Optimization Assessment

|  |
| --- |
| **Review control sequences to verify systems will maintain intended conditions during building operation.** |
| [ ]  | **Temperature –** Setpoints match design. |
| **Setpoint** | **Design** |
| [ ]  | **Humidity (if applicable) –** Setpoints match design.* Licensed professional to determine if setpoint should be adjusted to maintain a relative humidity between 40% and 60%.
 |
| **Setpoint** | **Design** |
| **Ventilation Schedule Operation**  |
| [ ]  | **Ventilation operates continuously during occupied hours.*** Occupied hours to include **all** hours building is occupied by staff or patrons (i.e. teachers, security, janitorial staff, night shift, etc.).
* Includes all exhaust fans and fans used to distribute outside air.
 |
| [ ]  | **Daily Flush*** Verify a daily flush is scheduled for 2 hours before and after scheduled occupancy **(or)**
 |
|  | * Demonstrate calculation of time for 3 air changes to reduce concentration of airborne infectious particles by 95% per ASHRAE Guidance for Building Readiness[[1]](#footnote-1) or otherwise applicable local or state guidance

**Calculated Flush Time =**  |
| [ ]  | **Deficiencies** - Document deficiencies, options for adjustment (i.e. Humidity) and recommendations for additional maintenance, replacement or upgrades. |
| [ ]  | Include relevant screenshots and photographic documentation |

*This document is intended to be used solely as an aide when developing the methods, procedures, and forms used in the Ventilation Verification and Energy Optimization Assessment.  It is the responsibility of each contractor, supervisor, and technician to ensure that the methods, procedures, and forms used meet the requirements of the local mechanical codes.  The National Energy Management Institute Committee makes no representations, whatsoever, that drafting procedures or forms based on this document will meet that requirement of local mechanical codes and expressly disclaims any liability or responsibility regarding the use of this document.*

1. ); ASHRAE, ASHRAE Epidemic Task Force: Building Readiness (updated May 22, 2020) (https://www.ashrae.org/file%20library/technical%20resources/covid-19/ashrae-building-readiness.pdf) [↑](#footnote-ref-1)